## JobCard
Final Inspection
Order Number | FSO190786
Project Name | Jeju Dream Tower III
Hood Item Number | 71.6 M1
Model | KVI
Final Inspection | Inspected By/Date
Check Items |  | Comment | Inspector Comments
Overall Length,Overall width and Overall height (Measure two side if possible) . |  |  | 口 Pass 口 NG
Spigot Size and Location are correct. |  |  | 口 Pass 口 NG
Catch Basin,drain hole,drain tap and drain valve are installed in correct location. |  |  | 口 Pass 口 NG
The dimension of Ansu pipes are in line with Ansul drawings. |  |  | 口 Pass 口 NG
The position of Marvel IR sensors are correct. |  |  | 口 Pass 口 NG
No scracth and deformation on visual surface, welding color and defects have been fixed. |  |  | 口 Pass 口 NG
Appearance is clean, no greasy dirty and useless parts. |  |  | 口 Pass 口 NG
The appearance of the hood is smooth, and the water washing hood is water collecting and flanging . |  |  | 口 Pass 口 NG
Mesh plates have no wave-like deformation. |  |  | 口 Pass 口 NG
The sharp edges of UV door and maintenance gate have been polished, no burrs and sharp edges. |  |  | 口 Pass 口 NG
Catch basin, drain tap and KSA filter can be easily installed and taken down. |  |  | 口 Pass 口 NG
The fit-up gaps of UV door,fluorescent lamp and top pannel are even. |  |  | 口 Pass 口 NG
Module jointing surface should be flat and match with other modules. |  |  | 口 Pass 口 NG
Bolts are firmly installed, no missing bolts. |  |  | 口 Pass 口 NG
Capture Jet fan is installed and good running. |  |  | 口 Pass 口 NG
Lights are installed and good running. |  |  | 口 Pass 口 NG
CJ Tap pressure need to be 60±5Pa. |  |  | 口 Pass 口 NG
UV system is installed and proper functioning (details in the SOP). UV warning signs have been posted on the UV door. |  |  | 口 Pass 口 NG
The mounting bracket shooting pin of the UV Rack of the UV hood has been welded and reinforced. |  |  | 口 Pass 口 NG
The type of UV control of UV hoods can meet the drawing. |  |  | 口 Pass 口 NG
If a project contains UV hoods,then all KSA filters and washing baffle plates of this project should be assemblied with magnets. |  |  | 口 Pass 口 NG
Ansul pipe watertight test has been done(sample inspection), keep 1.6Mpa pressure for 5min, no leakage. |  |  | 口 Pass 口 NG
Ansul system is installed according to the drawing. |  |  | 口 Pass 口 NG
Penetrant testing has been passed,no leakage. Washing pipes and spray nozzles are firmly assembled, the model of spray nozzles and angle are installed correctly. |  |  | 口 Pass 口 NG
MARVEL function test of hoods with MARVEL system is tested and qualified. |  |  | 口 Pass 口 NG
CMOD system of CMOD hood is tested and qualified. |  |  | 口 Pass 口 NG
Nameplate has been installed correctly and should be conformed with GB/T 13306-2-11. |  |  | 口 Pass 口 NG
Earth resistance of electric control box should be less than 2Ω. |  | (value) | 口 Pass 口 NG
Insulation resistance between plates should be greater than or equal to 50MΩ. |  | (value) | 口 Pass 口 NG
Insulation resistance between control box should be greater than or equal to 50MΩ. |  | (value) | 口 Pass 口 NG
Dielectric Voltage Withstand Test of UL hood is qualified.(voltage 1000Vac, duration 60S, or voltage 1200Vac, duration 1S, no damage and breakdown of insulator.) |  |  | 口 Pass 口 NG
Products satisfy inspection instruction and technology requirments. |  |  | 口 Pass 口 NG
Conclusion: