## JobCard
Final Inspection最终检验
Order Number 订单编号 | FSO190786
Project Name 项目名称 | Jeju Dream Tower III
Hood Item Number 烟罩项目号 | 71.6 M1
Model 型号 | KVI
Final Inspection 最终检验 | Inspected By/Date 检验人/日期
Check Items 栏目 |  | Comment 意见 | Inspector Comments 检验评论
Overall Length,Overall width and Overall height (Measure two side if possible) 总长度,总宽度和总高度（若条件允许，测两面） |  |  | 口 Pass 口 NG
Spigot Size and Location are correct 新风，排风口尺寸和位置正确。 |  |  | 口 Pass 口 NG
Catch Basin,drain hole,drain tap and drain valve are installed in correct location 集油槽,排水管，油塞，排水阀正确位置 |  |  | 口 Pass 口 NG
The dimension of Ansu pipes are in line with Ansul drawings.Ansul 管路尺寸与图纸一致。 |  |  | 口 Pass 口 NG
The position of Marvel IR sensors are correct. Marvel 红外探头位置正确。 |  |  | 口 Pass 口 NG
No scracth and deformation on visual surface, welding color and defects have been fixed.可视面无划伤、变形,焊斑、焊接缺陷已处理. |  |  | 口 Pass 口 NG
Appearance is clean, no greasy dirty and useless parts.外观干净，无油污、多余部件。 |  |  | 口 Pass 口 NG
The appearance of the hood is smooth, and the water washing hood is water collecting and flanging 烟罩外观打胶平整，水洗烟罩集水翻边内打防水胶。 |  |  | 口 Pass 口 NG
Mesh plates have no wave-like deformation. 网孔板无波浪变形。 |  |  | 口 Pass 口 NG
The sharp edges of UV door and maintenance gate have been polished, no burrs and sharp edges. UV门、风机检修门边已打磨，无毛刺或锐边。 |  |  | 口 Pass 口 NG
Catch basin, drain tap and KSA filter can be easily installed and taken down. 集油槽,油塞,KSA过滤器易安装和拆卸。 |  |  | 口 Pass 口 NG
The fit-up gaps of UV door,fluorescent lamp and top pannel are even. UV门/日光灯门/新风前盖板装配间隙均匀。 |  |  | 口 Pass 口 NG
Module jointing surface should be flat and match with other modules. 烟罩模块组拼面平整，且新风、排风、灯罩配合模块平齐。 |  |  | 口 Pass 口 NG
Bolts are firmly installed, no missing bolts. 螺栓已紧固，无遗失。 |  |  | 口 Pass 口 NG
Capture Jet fan is installed and good running. 捕捉风扇已装且正常运行。 |  |  | 口 Pass 口 NG
Lights are installed and good running. 照明已安装并正常运作。 |  |  | 口 Pass 口 NG
CJ Tap pressure need to be 60±5Pa.工作时，CJ Tap口处气压应为60±5Pa。 |  |  | 口 Pass 口 NG
UV system is installed and proper functioning (details in the SOP). UV warning signs have been posted on the UV door. UV系统已安装并正常运作(详见SOP)，UV警示标识已张贴在UV门上。 |  |  | 口 Pass 口 NG
The mounting bracket shooting pin of the UV Rack of the UV hood has been welded and reinforced. UV烟罩的UV Rack的安装支架 射钉已焊接加固。 |  |  | 口 Pass 口 NG
The type of UV control of UV hoods can meet the drawing. UV烟罩的UV控制器型号符合图纸要求。 |  |  | 口 Pass 口 NG
If a project contains UV hoods,then all KSA filters and washing baffle plates of this project should be assemblied with magnets. 含UV烟罩的项目，所有KSA过滤器和水洗挡板上的磁铁已安装。 |  |  | 口 Pass 口 NG
Ansul pipe watertight test has been done(sample inspection), keep 1.6Mpa pressure for 5min, no leakage. Ansul管路漏水测试（抽检），打压1.6Mpa保压5min，管路无漏水。 |  |  | 口 Pass 口 NG
Ansul system is installed according to the drawing. Ansul已按图纸安装。 |  |  | 口 Pass 口 NG
Penetrant testing has been passed,no leakage. Washing pipes and spray nozzles are firmly assembled, the model of spray nozzles and angle are installed correctly. 水洗烟罩渗透剂已喷，无渗漏。水洗管及喷头装配牢固，喷头型号及角度安装正确。 |  |  | 口 Pass 口 NG
MARVEL function test of hoods with MARVEL system is tested and qualified.带MARVEL烟罩的MARVEL系统功能测试合格。 |  |  | 口 Pass 口 NG
CMOD system of CMOD hood is tested and qualified. CMOD烟罩的CMOD系统功能测试合格。 |  |  | 口 Pass 口 NG
Nameplate has been installed correctly and should be conformed with GB/T 13306-2-11. 铭牌已正确安装，铭牌符合GB/T 13306-2011。 |  |  | 口 Pass 口 NG
Earth resistance of electric control box should be less than 2Ω. 电气控制箱接地电阻小于2Ω。 |  | (填实际值) | 口 Pass 口 NG
Insulation resistance between plates should be greater than or equal to 50MΩ. 极板间绝缘电阻≥50MΩ。 |  | (填实际值) | 口 Pass 口 NG
Insulation resistance between control box should be greater than or equal to 50MΩ. 控制箱绝缘电阻≥50MΩ。 |  | (填实际值) | 口 Pass 口 NG
Dielectric Voltage Withstand Test of UL hood is qualified.(voltage 1000Vac, duration 60S, or voltage 1200Vac, duration 1S, no damage and breakdown of insulator.) UL烟罩绝缘耐压测试合格。 (电压1000Vac,持续60S，或电压1200Vac,持续1S，绝缘体无破损、无击穿。) |  |  | 口 Pass 口 NG
Products satisfy inspection instruction and technology requirments.产品满足检验作业指导书和技术要求。 |  |  | 口 Pass 口 NG
Conclusion 检验结论: