## JobCard
Production Order Cover Sheet
Order Number 订单编号 |  | FSO190786
Project Name 项目名称 |  | Jeju Dream Tower III
Hood Item Number 烟罩项目号 |  | 71.6 M1
Model 型号 |  | KVI
Project Type 项目类型 |  | 国内
Project record(项目记录) |  | Date 日期 | Initials 署名 |  |  | Shipping Time
Project | Enterer (Project Manager) 项目录入 |  |  |  |  | 发货时间
Document Reelase 资料发布 | [5 empty] | 2019-12-27
Document Re-check 资料复核
Project | Purchasing 采购部
Approve | Tech. 技术部
项目审核 | Prod. 生产部
Product Description 产品描述 |  | Model 型号 | Detail Code | Length 长 | Width 宽 | Height 高 | SidePanel 侧板
| 71.6 M1 | KVI | M1 | 2050 | 1500 | 555 | Left
Accessories List
配件清单
Tech. Special Notes
技术部 特别注释
Production Record 生产过程记录 |  | Date 日期 | Comments 有无异常 |  |  | Labor 人工 | Sign 签名
Laser/punch breaker cutting 激光切割/冲床切割
Bending 折弯
cutting film & parts collection 切膜&配料
Welding Assembly 焊接
Polishing 抛光
Hood Assembly 结构装配
Ansul pre-piping Ansul预埋管装配
Water Washing piping 水洗管装配
Electrical Assembly 电气装配
Assembly Inspection组装检验
Packaging 打包
Process Inspection 1 过程检验1
Order Number 订单编号 |  | FSO190786
Project Name 项目名称 |  | Jeju Dream Tower III
Hood Item Number 烟罩项目号 |  | 71.6 M1
Model 型号 |  | KVI
[5 empty] | Confirm 确认 | Conclusion 检验结论 | Corrections 更正
Cutting Inspection (Laser & punch breaker)下料检验 (激光切割/数控冲操作员) /Inspected Date 检查日期:
first part check 首件尺寸检验
right drawing direction 零件拉丝方向正确
No damage on the film 贴膜无损伤
Parts are free of scratches and dents 零件没有划痕和凹痕
Parts are free of burrs and sharp edges (laser) 零件没有毛刺和尖锐突出
Bending Inspection (bender) 折弯检验 (折弯操作员 /Inspected Date 检查日期:
drawing direction correct 零件拉丝方向正确
bent surface correct 折弯表面正确
bent dimension correct 折弯尺寸正确
No damage on the film 贴膜无损伤
Parts are free of scratches and dents 零件没有划痕和凹痕
Parts are free of burrs and sharp edges (laser) 零件没有毛刺和尖锐突出
cutting film & parts collection 切膜&配料检验 (切膜配料员) /Inspected Date 检查日期:
No damage on the film 贴膜无损伤
Parts are free of scratches and dents 零件没有划痕和凹痕
Parts are free of burrs and sharp edges (laser) 零件没有毛刺和尖锐突出
All parts are included 已包含所有 零件
Welding Inspection (welder) 焊接检验 (焊工)/Inspected Date 检查日期:
Exhaust Beam assembled dimensions correct 排风口主粱结构装配尺寸正确
Exhaust Beam welds no voids or gaps 排风口主粱焊接无缝隙
No twisty deformation in length direction 排风口组件无扭曲变形(对角线尺寸一致)
No visible deformation around welding area 排风口焊缝周围无明显变形
Supply Beam assembled dimensions correct 新风口主粱结构装配尺寸正确
Supply Beam welds no voids or gaps 新风口主粱焊接无缝隙
No twisty deformation in length direction 新风口组件无扭曲变形(对角线尺寸一致)
No visible deformation around welding area 新风口焊缝周围无明显变形
side panel assembled dimensions correct 侧板结构装配尺寸正确
side panel welds no voids or gaps 侧板焊接无缝隙
No twisty deformation in length direction 侧板无扭曲变形(对角线尺寸一致)
No visible deformation around welding area 侧板焊缝周围无明显变形
Process Inspection 2 过程检验2
Order Number 订单编号 |  | FSO190786
Project Name 项目名称 |  | Jeju Dream Tower III
Hood Item Number 烟罩项目号 |  | 71.6 M1
Model 型号 |  | KVI
[5 empty] | Confirm 确认 | Conclusion 检验结论 | Corrections 更正
Polishing Inspection (polisher) 磨光检验 (磨光操作员) /Inspected Date 检查日期:
Exhaust Beam blend no more than 12mm 排风口主粱抛光区域控制在12mm之内
Supply Beam blend no more than 12mm 新风口主粱抛光区域控制在12mm之内
side panel blend no more than 12mm 侧板抛光区域控制在12mm之内
Assembly Inspection 组装检验 (team leader)/Inspected Date 检查日期:
Overall Length 总长度
Overall Width 总宽度
Overall Height 总高度
Air supply spigot size and location correct 新风口尺寸及位置正确
exhaust spigot size and location correct 排风口尺寸及位置正确
All screw fixed 所有螺丝已经旋紧固定
All plugs inserted 所有塞子已经插入
Catch Basin Installed in correct location 集油槽已安装在正确位置
Catch Basin Installs and removes easily 集油槽易于安装和拆卸
Capture Jet Fan installed / function 捕捉风扇已安装/可运行
Lighting installed and functions 照明已安装并正常运作
UV console installed and functions UV控制器已安装并正常运作
UV system installed and functions UV系统已安装并正常运作
Water leak test for KW/UW hood (no leaking in welding area and piping) 漏水测试（焊缝和管路没有漏水发生）
Water leak check for UVR (no water leaking in UV tubes,terminals) 漏水测试（UV灯管和电缆接头出无漏水）
KSA filters install and remove easily KSA过滤器易于安装和拆卸
KSA filters free of sharp edges KSA过滤器没有尖锐棱角
No open gaps in hood assembly 烟罩组装没有过大缝隙
No Scratches or dents 可见表面无划痕或凹痕
Visible welds cleaned 焊接处已清理
Polishing blended 抛光区域平整和美观
Unit caulked neat and no smears 装填缝平整,无污点
Front panel installed flush without excessive gaps 前板安装紧固,无过大间隙
light doors operate without excess gaps 日光灯门操作时无过大间隙
access doors fixed with right drawing direction 检修门的拉丝方向是否正确
Overall appearance is clean 外观干净
Accessory put in 附件放入包装:
special request 特别要求：
Option 意见:
Final Inspection最终检验
Order Number 订单编号 |  | FSO190786
Project Name 项目名称 |  | Jeju Dream Tower III
Hood Item Number 烟罩项目号 |  | 71.6 M1
Model 型号 |  | KVI
Final Inspection 最终检验 |  | Inspected By/Date 检验人/日期
Check Items 栏目 |  |  |  |  | Comment 意见 | Inspector Comments 检验评论
Overall Length,Overall width and Overall height (Measure two side if possible) 总长度,总宽度和总高度（若条件允许，测两面） | [5 empty] | 口 Pass 口 NG
Spigot Size and Location are correct 新风，排风口尺寸和位置正确。 | [5 empty] | 口 Pass 口 NG
Catch Basin,drain hole,drain tap and drain valve are installed in correct location 集油槽,排水管，油塞，排水阀正确位置 | [5 empty] | 口 Pass 口 NG
The dimension of Ansu pipes are in line with Ansul drawings.Ansul 管路尺寸与图纸一致。 | [5 empty] | 口 Pass 口 NG
The position of Marvel IR sensors are correct. Marvel 红外探头位置正确。 | [5 empty] | 口 Pass 口 NG
No scracth and deformation on visual surface, welding color and defects have been fixed.可视面无划伤、变形,焊斑、焊接缺陷已处理. | [5 empty] | 口 Pass 口 NG
Appearance is clean, no greasy dirty and useless parts.外观干净，无油污、多余部件。 | [5 empty] | 口 Pass 口 NG
The appearance of the hood is smooth, and the water washing hood is water collecting and flanging 烟罩外观打胶平整，水洗烟罩集水翻边内打防水胶。 | [5 empty] | 口 Pass 口 NG
Mesh plates have no wave-like deformation. 网孔板无波浪变形。 | [5 empty] | 口 Pass 口 NG
The sharp edges of UV door and maintenance gate have been polished, no burrs and sharp edges. UV门、风机检修门边已打磨，无毛刺或锐边。 | [5 empty] | 口 Pass 口 NG
Catch basin, drain tap and KSA filter can be easily installed and taken down. 集油槽,油塞,KSA过滤器易安装和拆卸。 | [5 empty] | 口 Pass 口 NG
The fit-up gaps of UV door,fluorescent lamp and top pannel are even. UV门/日光灯门/新风前盖板装配间隙均匀。 | [5 empty] | 口 Pass 口 NG
Module jointing surface should be flat and match with other modules. 烟罩模块组拼面平整，且新风、排风、灯罩配合模块平齐。 | [5 empty] | 口 Pass 口 NG
Bolts are firmly installed, no missing bolts. 螺栓已紧固，无遗失。 | [5 empty] | 口 Pass 口 NG
Capture Jet fan is installed and good running. 捕捉风扇已装且正常运行。 | [5 empty] | 口 Pass 口 NG
Lights are installed and good running. 照明已安装并正常运作。 | [5 empty] | 口 Pass 口 NG
CJ Tap pressure need to be 60±5Pa.工作时，CJ Tap口处气压应为60±5Pa。 | [5 empty] | 口 Pass 口 NG
UV system is installed and proper functioning (details in the SOP). UV warning signs have been posted on the UV door. UV系统已安装并正常运作(详见SOP)，UV警示标识已张贴在UV门上。 | [5 empty] | 口 Pass 口 NG
The mounting bracket shooting pin of the UV Rack of the UV hood has been welded and reinforced. UV烟罩的UV Rack的安装支架 射钉已焊接加固。 | [5 empty] | 口 Pass 口 NG
The type of UV control of UV hoods can meet the drawing. UV烟罩的UV控制器型号符合图纸要求。 | [5 empty] | 口 Pass 口 NG
If a project contains UV hoods,then all KSA filters and washing baffle plates of this project should be assemblied with magnets. 含UV烟罩的项目，所有KSA过滤器和水洗挡板上的磁铁已安装。 | [5 empty] | 口 Pass 口 NG
Ansul pipe watertight test has been done(sample inspection), keep 1.6Mpa pressure for 5min, no leakage. Ansul管路漏水测试（抽检），打压1.6Mpa保压5min，管路无漏水。 | [5 empty] | 口 Pass 口 NG
Ansul system is installed according to the drawing. Ansul已按图纸安装。 | [5 empty] | 口 Pass 口 NG
Penetrant testing has been passed,no leakage. Washing pipes and spray nozzles are firmly assembled, the model of spray nozzles and angle are installed correctly. 水洗烟罩渗透剂已喷，无渗漏。水洗管及喷头装配牢固，喷头型号及角度安装正确。 | [5 empty] | 口 Pass 口 NG
MARVEL function test of hoods with MARVEL system is tested and qualified.带MARVEL烟罩的MARVEL系统功能测试合格。 | [5 empty] | 口 Pass 口 NG
CMOD system of CMOD hood is tested and qualified. CMOD烟罩的CMOD系统功能测试合格。 | [5 empty] | 口 Pass 口 NG
Nameplate has been installed correctly and should be conformed with GB/T 13306-2-11. 铭牌已正确安装，铭牌符合GB/T 13306-2011。 | [5 empty] | 口 Pass 口 NG
Earth resistance of electric control box should be less than 2Ω. 电气控制箱接地电阻小于2Ω。 |  |  |  |  | (填实际值) | 口 Pass 口 NG
Insulation resistance between plates should be greater than or equal to 50MΩ. 极板间绝缘电阻≥50MΩ。 |  |  |  |  | (填实际值) | 口 Pass 口 NG
Insulation resistance between control box should be greater than or equal to 50MΩ. 控制箱绝缘电阻≥50MΩ。 |  |  |  |  | (填实际值) | 口 Pass 口 NG
Dielectric Voltage Withstand Test of UL hood is qualified.(voltage 1000Vac, duration 60S, or voltage 1200Vac, duration 1S, no damage and breakdown of insulator.) UL烟罩绝缘耐压测试合格。 (电压1000Vac,持续60S，或电压1200Vac,持续1S，绝缘体无破损、无击穿。) | [5 empty] | 口 Pass 口 NG
Products satisfy inspection instruction and technology requirments.产品满足检验作业指导书和技术要求。 | [5 empty] | 口 Pass 口 NG
Conclusion 检验结论:
Key Components Batch No. Record 关键元器件批号记录表
Order Number 订单编号 |  | FSO190786
Project Name 项目名称 |  | Jeju Dream Tower III
Hood Item Number 烟罩项目号 |  | 71.6 M1
Model 型号 |  | KVI
关键元器件 |  | 产品 |  | 型号 | 批号 | 登记人 | 日期
Key Component |  | Proudct |  | Model | Bath No. | Recorder | Date
UVC控制器 |  | Hood 烟罩
Mesh过滤器 |  | Hood 烟罩
KSA过滤器 |  | Hood 烟罩
UV灯 |  | Hood 烟罩
烟罩风机 |  | Hood 烟罩
控制器（包含镇流器） |  | Hood 烟罩
UV灯 |  | Pollustop
袋式过滤单元 |  | Pollustop
高效（HEAP）过滤单元 |  | Pollustop
活性炭过滤单元 |  | Pollustop
板式过滤单元 |  | Pollustop
变频风机 |  | Pollustop
Order Number 订单编号 |  | FSO190786
Project Name 项目名称 |  | Jeju Dream Tower III
Hood Item Number 烟罩序列号 |  | 71.6 M1
Model 型号 |  | KVI
Module Size 单元尺寸 |  | 2050 | X | 1500 | X | 555 | mm
Order Number 订单编号 |  | FSO190786
Project Name 项目名称 |  | Jeju Dream Tower III
Hood Item Number 烟罩序列号 |  | 71.6 M1
Model 型号 |  | KVI
Module Size 单元尺寸 |  | 2050 | X | 1500 | X | 555 | mm