## JobCard
Production Order Cover Sheet
Order Number 订单编号 |  | FSO190786
Project Name 项目名称 |  | Jeju Dream Tower III
Hood Item Number 烟罩项目号 |  | 71.6 M1
Model 型号 |  | KVI
Project Type 项目类型 |  | 国内
Project record(项目记录) |  | Date 日期 | Initials 署名 |  |  | Shipping Time
Project | Enterer (Project Manager) 项目录入 |  |  |  |  | 发货时间
Document Reelase 资料发布 | [5 empty] | 2019-12-27
Document Re-check 资料复核
Project | Purchasing 采购部
Approve | Tech. 技术部
项目审核 | Prod. 生产部
Product Description 产品描述 |  | Model 型号 | Detail Code | Length 长 | Width 宽 | Height 高 | SidePanel 侧板
| 71.6 M1 | KVI | M1 | 2050 | 1500 | 555 | Left
Accessories List
配件清单
Tech. Special Notes
技术部 特别注释
2 |  | Date 日期 | Comments 有无异常 |  |  | Labor 人工 | Sign 签名
Laser/punch breaker cutting 激光切割/冲床切割
Bending 折弯
cutting film & parts collection 切膜&配料
Welding Assembly 焊接
Polishing 抛光
Hood Assembly 结构装配
Ansul pre-piping Ansul预埋管装配
Water Washing piping 水洗管装配
Electrical Assembly 电气装配
Assembly Inspection组装检验
Packaging 打包
Process Inspection 1 过程检验1
Order Number 订单编号 |  | FSO190786
Project Name 项目名称 |  | Jeju Dream Tower III
Hood Item Number 烟罩项目号 |  | 71.6 M1
Model 型号 |  | KVI
[5 empty] | Confirm 确认 | Conclusion 检验结论 | Corrections 更正
Cutting Inspection (Laser & punch breaker)下料检验 (激光切割/数控冲操作员) /Inspected Date 检查日期:
first part check 首件尺寸检验
right drawing direction 零件拉丝方向正确
No damage on the film 贴膜无损伤
Parts are free of scratches and dents 零件没有划痕和凹痕
Parts are free of burrs and sharp edges (laser) 零件没有毛刺和尖锐突出
Bending Inspection (bender) 折弯检验 (折弯操作员 /Inspected Date 检查日期:
drawing direction correct 零件拉丝方向正确
bent surface correct 折弯表面正确
bent dimension correct 折弯尺寸正确
No damage on the film 贴膜无损伤
Parts are free of scratches and dents 零件没有划痕和凹痕
Parts are free of burrs and sharp edges (laser) 零件没有毛刺和尖锐突出
cutting film & parts collection 切膜&配料检验 (切膜配料员) /Inspected Date 检查日期:
No damage on the film 贴膜无损伤
Parts are free of scratches and dents 零件没有划痕和凹痕
Parts are free of burrs and sharp edges (laser) 零件没有毛刺和尖锐突出
All parts are included 已包含所有 零件
Welding Inspection (welder) 焊接检验 (焊工)/Inspected Date 检查日期:
Exhaust Beam assembled dimensions correct 排风口主粱结构装配尺寸正确
Exhaust Beam welds no voids or gaps 排风口主粱焊接无缝隙
No twisty deformation in length direction 排风口组件无扭曲变形(对角线尺寸一致)
No visible deformation around welding area 排风口焊缝周围无明显变形
Supply Beam assembled dimensions correct 新风口主粱结构装配尺寸正确
Supply Beam welds no voids or gaps 新风口主粱焊接无缝隙
No twisty deformation in length direction 新风口组件无扭曲变形(对角线尺寸一致)
No visible deformation around welding area 新风口焊缝周围无明显变形
side panel assembled dimensions correct 侧板结构装配尺寸正确
side panel welds no voids or gaps 侧板焊接无缝隙
No twisty deformation in length direction 侧板无扭曲变形(对角线尺寸一致)
No visible deformation around welding area 侧板焊缝周围无明显变形
Process Inspection 2 过程检验2
Order Number 订单编号 |  | FSO190786
Project Name 项目名称 |  | Jeju Dream Tower III
Hood Item Number 烟罩项目号 |  | 71.6 M1
Model 型号 |  | KVI
[5 empty] | Confirm 确认 | Conclusion 检验结论 | Corrections 更正
Polishing Inspection (polisher) 磨光检验 (磨光操作员) /Inspected Date 检查日期:
Exhaust Beam blend no more than 12mm 排风口主粱抛光区域控制在12mm之内
Supply Beam blend no more than 12mm 新风口主粱抛光区域控制在12mm之内
side panel blend no more than 12mm 侧板抛光区域控制在12mm之内
Assembly Inspection 组装检验 (team leader)/Inspected Date 检查日期:
Overall Length 总长度
Overall Width 总宽度
Overall Height 总高度
Air supply spigot size and location correct 新风口尺寸及位置正确
exhaust spigot size and location correct 排风口尺寸及位置正确
All screw fixed 所有螺丝已经旋紧固定
All plugs inserted 所有塞子已经插入
Catch Basin Installed in correct location 集油槽已安装在正确位置
Catch Basin Installs and removes easily 集油槽易于安装和拆卸
Capture Jet Fan installed / function 捕捉风扇已安装/可运行
Lighting installed and functions 照明已安装并正常运作
UV console installed and functions UV控制器已安装并正常运作
UV system installed and functions UV系统已安装并正常运作
Water leak test for KW/UW hood (no leaking in welding area and piping) 漏水测试（焊缝和管路没有漏水发生）
Water leak check for UVR (no water leaking in UV tubes,terminals) 漏水测试（UV灯管和电缆接头出无漏水）
KSA filters install and remove easily KSA过滤器易于安装和拆卸
KSA filters free of sharp edges KSA过滤器没有尖锐棱角
No open gaps in hood assembly 烟罩组装没有过大缝隙
No Scratches or dents 可见表面无划痕或凹痕
Visible welds cleaned 焊接处已清理
Polishing blended 抛光区域平整和美观
Unit caulked neat and no smears 装填缝平整,无污点
Front panel installed flush without excessive gaps 前板安装紧固,无过大间隙
light doors operate without excess gaps 日光灯门操作时无过大间隙
access doors fixed with right drawing direction 检修门的拉丝方向是否正确
Overall appearance is clean 外观干净
Accessory put in 附件放入包装:
special request 特别要求：
Option 意见:
Final Inspection
Order Number |  | FSO190786
Project Name |  | Jeju Dream Tower III
Hood Item Number |  | 71.6 M1
Model |  | KVI
Final Inspection |  | Inspected By/Date
Check Items |  |  |  |  | Comment | Inspector Comments
Overall Length,Overall width and Overall height (Measure two side if possible). | [5 empty] | 口 Pass 口 NG
Spigot Size and Location are correct. | [5 empty] | 口 Pass 口 NG
Catch Basin,drain hole,drain tap and drain valve are installed in correct location. | [5 empty] | 口 Pass 口 NG
The dimension of Ansu pipes are in line with Ansul drawings. | [5 empty] | 口 Pass 口 NG
The position of Marvel IR sensors are correct. | [5 empty] | 口 Pass 口 NG
No scracth and deformation on visual surface, welding color and defects have been fixed. | [5 empty] | 口 Pass 口 NG
Appearance is clean, no greasy dirty and useless parts. | [5 empty] | 口 Pass 口 NG
The appearance of the hood is smooth, and the water washing hood is water collecting and flanging . | [5 empty] | 口 Pass 口 NG
Mesh plates have no wave-like deformation. | [5 empty] | 口 Pass 口 NG
The sharp edges of UV door and maintenance gate have been polished, no burrs and sharp edges. | [5 empty] | 口 Pass 口 NG
Catch basin, drain tap and KSA filter can be easily installed and taken down. | [5 empty] | 口 Pass 口 NG
The fit-up gaps of UV door,fluorescent lamp and top pannel are even. | [5 empty] | 口 Pass 口 NG
Module jointing surface should be flat and match with other modules. | [5 empty] | 口 Pass 口 NG
Bolts are firmly installed, no missing bolts. | [5 empty] | 口 Pass 口 NG
Capture Jet fan is installed and good running. | [5 empty] | 口 Pass 口 NG
Lights are installed and good running. | [5 empty] | 口 Pass 口 NG
CJ Tap pressure need to be 60±5Pa. | [5 empty] | 口 Pass 口 NG
UV system is installed and proper functioning (details in the SOP). UV warning signs have been posted on the UV door. | [5 empty] | 口 Pass 口 NG
The mounting bracket shooting pin of the UV Rack of the UV hood has been welded and reinforced. | [5 empty] | 口 Pass 口 NG
The type of UV control of UV hoods can meet the drawing. | [5 empty] | 口 Pass 口 NG
If a project contains UV hoods,then all KSA filters and washing baffle plates of this project should be assemblied with magnets. | [5 empty] | 口 Pass 口 NG
Ansul pipe watertight test has been done(sample inspection), keep 1.6Mpa pressure for 5min, no leakage. | [5 empty] | 口 Pass 口 NG
Ansul system is installed according to the drawing. | [5 empty] | 口 Pass 口 NG
Penetrant testing has been passed,no leakage. Washing pipes and spray nozzles are firmly assembled, the model of spray nozzles and angle are installed correctly. | [5 empty] | 口 Pass 口 NG
MARVEL function test of hoods with MARVEL system is tested and qualified. | [5 empty] | 口 Pass 口 NG
CMOD system of CMOD hood is tested and qualified. | [5 empty] | 口 Pass 口 NG
Nameplate has been installed correctly and should be conformed with GB/T 13306-2-11. | [5 empty] | 口 Pass 口 NG
Earth resistance of electric control box should be less than 2Ω. |  |  |  |  | (value) | 口 Pass 口 NG
Insulation resistance between plates should be greater than or equal to 50MΩ. |  |  |  |  | (value) | 口 Pass 口 NG
Insulation resistance between control box should be greater than or equal to 50MΩ. |  |  |  |  | (value) | 口 Pass 口 NG
Dielectric Voltage Withstand Test of UL hood is qualified.(voltage 1000Vac, duration 60S, or voltage 1200Vac, duration 1S, no damage and breakdown of insulator.) | [5 empty] | 口 Pass 口 NG
Products satisfy inspection instruction and technology requirments. | [5 empty] | 口 Pass 口 NG
Conclusion:
Order Number |  | FSO190786
Project Name |  | Jeju Dream Tower III
Hood Item Number |  | 71.6 M1
Model |  | KVI
Module Size |  | 2050 | X | 1500 | X | 555 | mm
Order Number |  | FSO190786
Project Name |  | Jeju Dream Tower III
Hood Item Number |  | 71.6 M1
Model |  | KVI
Module Size |  | 2050 | X | 1500 | X | 555 | mm